## Tabelle1
Name |  |  |  | Datentyp | Startwert | Istwert | Rem | Erreichbar | Sichtbar | Einstellwert | Kommentar
Element1_OUT |  |  |  | ANA_OUT |  |  | False | True | True | False
|  | Config |  | Struct |  |  | False | False | False | False
|  |  | Enable | Bool | false | FALSE | False | False | False | False | element enabled
|  |  | AOT_Mode | Int | 0 | 0 | False | False | False | False | mode for AOT (1: 4..20mA, 3: P&F)
|  |  | PAW | Int | 0 | 0 | False | False | False | False | PEW of AIN
|  |  | GOP_Open | Bool | false | FALSE | False | False | False | False | limit switch open exists
|  |  | GOS_Closed | Bool | false | FALSE | False | False | False | False | limit switch closeed exists
|  |  | Broken_Wire_Current | Int | 300 | 300 | False | False | False | False | broken wire current (1/100 mA)
|  | STATUS |  | FIX_KEY |  |  | False | True | True | False | status of the measurement
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | TRUE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | TRUE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | TRUE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | TRUE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | TRUE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | TRUE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | TRUE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | TRUE | False | True | True | False | switched on
|  |  | OUT_VALUE | Int | 0 | 1 | False | True | True | False | output [0...10000 = 0...100.00%]
|  |  | SERVICE_SET | Int | 0 | 2 | False | True | True | False | service setpoint [0...10000 = 0...100%]
|  |  | SET_VALUE | Int | 0 | 3 | False | True | True | False | FV setpoint from recipe [0...10000 = 0...100%]
|  |  | TIME_OPEN_SET | Int | 0 | 4 | False | True | True | False | max runtime for opening [s]
|  |  | TIME_CLOSE_SET | Int | 0 | 5 | False | True | True | False | max runtime for closing [s]
|  |  | TIME_OPEN_ACT | Int | 0 | 6 | False | True | True | False | act runtime for opening [s]
|  |  | TIME_CLOSE_ACT | Int | 0 | 7 | False | True | True | False | act runtime for closing [s]
|  |  | LOW_RANGE | Int | 0 | 0 | False | False | False | False | low range (output =0)
|  |  | HIGH_RANGE | Int | 10000 | 10000 | False | False | False | False | high range (output = 10000)
|  |  | SETPOINT_AUTO | Int | 0 | 0 | False | False | False | False | setpoint for automatic mode (low range ... high range)
|  |  | SETPOINT_MAN | Int | 0 | 0 | False | False | False | False | setpoint for manual mode (low range ... high range)
|  |  | AUTO_ON | Bool | false | FALSE | False | False | False | False | command for opening in automatic mode
|  |  | MAN_ON | Bool | false | FALSE | False | False | False | False | command for opening in maual mode
|  |  | SERVICE_ON | Bool | false | FALSE | False | False | False | False | command for opening in service mode
|  |  | IS_OPEN | Bool | false | FALSE | False | False | False | False | DIN is open
|  |  | IS_CLOSED | Bool | false | FALSE | False | False | False | False | DIN is closed
|  |  | VALVE_OUT | Bool | false | FALSE | False | False | False | False | DOT for VALVE_OUT
|  |  | KEEP_CLOSED | Bool | false | FALSE | False | False | False | False | keep closed (for bed burst)
|  | Alarm |  | typeAlarm |  |  | False | True | True | False
|  |  | PLCIntern | Byte | 16#0 | 16#99 | False | True | True | False
|  |  | ToSCADA | Byte | 16#0 | 16#99 | False | True | True | False
|  |  | FromSCADA | Byte | 16#0 | 16#99 | False | True | True | False
| Element1_VALUE |  |  | ANA_VALUE |  |  | False | True | True | False
|  | Config |  | Struct |  |  | False | False | False | False
|  |  | Enable | Bool | false | FALSE | False | False | False | False | element enabled
|  |  | AIN_Mode | Int | 1 | 1 | False | False | False | False | mode for AIN (1: 4..20mA, 2: PT100, 3: P&F)
|  |  | PEW | Int | 0 | 0 | False | False | False | False | PEW of AIN
|  |  | Low_Range | Int | 0 | 0 | False | False | False | False | Low Range for analog input
|  |  | High_Range | Int | 1500 | 1500 | False | False | False | False | High Range for analog input
|  |  | Broken_Wire_Current | Int | 300 | 300 | False | False | False | False | broken wire current (1/100 mA)
|  | STATUS |  | FIX_KEY |  |  | False | True | True | False | status of the measurement
|  |  | motor_forward | Bool | false | TRUE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | TRUE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | TRUE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | TRUE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | TRUE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | TRUE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | TRUE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | TRUE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | TRUE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | TRUE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | TRUE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | TRUE | False | True | True | False | internal
|  |  | imp_off | Bool | false | TRUE | False | True | True | False | internal
|  |  | imp_on | Bool | false | TRUE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | TRUE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | TRUE | False | True | True | False | switched on
|  | SENSOR |  | FIX_KEY |  |  | False | True | True | False | visualize sensor
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | TRUE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | TRUE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | TRUE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | TRUE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | TRUE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | TRUE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | TRUE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | TRUE | False | True | True | False | switched on
|  |  | ACT_VALUE | Int | 0 | 200 | False | True | True | False | actual value
|  |  | SET_VALUE | Int | 0 | 201 | False | True | True | False | setpoint from recipe
|  |  | MP_SET_VALUE | Int | 0 | 202 | False | True | True | False | machine paramter setpoint
|  |  | MIN_VALUE | Int | 0 | 203 | False | True | True | False | min limit value
|  |  | MIN_MIN_VALUE | Int | 0 | 204 | False | True | True | False | min min limit value
|  |  | MAX_VALUE | Int | 0 | 205 | False | True | True | False | max limit value
|  |  | MAX_MAX_VALUE | Int | 0 | 206 | False | True | True | False | max max limit value
|  |  | SET_STIME | Int | 180 | 207 | False | True | True | False | setpoint for alarm settling time [s]
|  |  | SET_DTIME_MIN | Int | 30 | 208 | False | True | True | False | setpoint for min alarm delay time [s]
|  |  | SET_DTIME_MAX | Int | 30 | 209 | False | True | True | False | setpoint for max alarm delay time [s]
|  |  | SET_DTIME_BROKEN_WIRE | Int | 5 | 210 | False | True | True | False | setpoint for broken wire alarm delay time [s]
|  |  | ACT_STIME | Int | 0 | 211 | False | True | True | False | actual value of alarm settling time [s]
|  |  | ACT_DTIME_MIN | Int | 0 | 212 | False | True | True | False | actual value of min alarm delay time [s]
|  |  | ACT_DTIME_MAX | Int | 0 | 213 | False | True | True | False | actual value of max alarm delay time [s]
|  |  | ACT_DTIME_BROKEN_WIRE | Int | 0 | 214 | False | True | True | False | actual value of broken wire alarm delay time [s]
|  |  | TRIP_VALUE | Int | 0 | 215 | False | True | True | False | trip value
|  | PID |  | Struct |  |  | False | True | True | False
|  | MANUAL_KEY |  | FIX_KEY |  |  | False | True | True | False | switching to manual mode
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | TRUE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | TRUE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | TRUE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | TRUE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | TRUE | False | True | True | False | internal
|  |  | imp_on | Bool | false | TRUE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | TRUE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | TRUE | False | True | True | False | switched on
|  |  | MODE | Int | 0 | 220 | False | True | True | False | modus controller
|  |  | SET_AUTO | Int | 0 | 221 | False | True | True | False | setpoint (auto) for controller
|  |  | SET_MAN | Int | 0 | 222 | False | True | True | False | output value of controller in manual mode
|  |  | SET_START | Int | 0 | 223 | False | True | True | False | output value of controller in start mode
|  |  | SET_FV | Int | 0 | 224 | False | True | True | False | output value of controller in forced mode
|  |  | SPARE | Int | 0 | 225 | False | True | True | False | output value of controller in revision mode
|  |  | P | Int | 4500 | 226 | False | True | True | False | PID parameter: P
|  |  | I | Int | 600 | 227 | False | True | True | False | PID parameter: I
|  |  | D | Int | 0 | 228 | False | True | True | False | PID parameter: D
|  |  | CONTRL_OUT | Int | 0 | 229 | False | True | True | False | output of controller (Y)
|  |  | TREND_SET_VALUE | Int | 0 | 230 | False | True | True | False | copy of SET_AUTO for trending
|  |  | CONTRL_ON | Bool | false | TRUE | False | True | True | False | controller is on
|  |  | MAN_ON | Bool | false | TRUE | False | True | True | False | manual mode on
|  |  | START_ON | Bool | false | TRUE | False | True | True | False | start mode on
|  |  | FV_ON | Bool | false | TRUE | False | True | True | False | forced mode on
|  |  | FREZ_ON | Bool | false | TRUE | False | True | True | False | freeze on
|  |  | SERVICE_ON | Bool | false | TRUE | False | True | True | False | service mode on
|  |  | OLD_IN_SET | Int | 0 | 0 | False | False | False | False | old setpoint for min/max alarm check
|  |  | INT_SCALE_OUT | Int | 0 | 0 | False | False | False | False | measurement scale out as integer
|  |  | REAL_SCALE_OUT | Real | 0 | 0 | False | False | False | False | measurement scale out as real
|  |  | BROKEN_WIRE | Bool | false | FALSE | False | False | False | False | wire broken, written in OB35, read in OB1
|  |  | CHK_MIN_0 | Bool | false | FALSE | False | False | False | False | also check if MIN value is "0"
|  |  | CHK_MAX_0 | Bool | false | FALSE | False | False | False | False | also check if MAX value is "0"
|  |  | EN_ALM_MIN | Bool | false | FALSE | False | False | False | False | enable alarm minimum
|  |  | EN_ALM_MIN_MIN | Bool | false | FALSE | False | False | False | False | enable alarm minimum minimum
|  |  | EN_ALM_MAX | Bool | false | FALSE | False | False | False | False | enable alarm maximum
|  |  | EN_ALM_MAX_MAX | Bool | false | FALSE | False | False | False | False | enable alarm maximum maximum
|  |  | EN_ALM_BROKEN_WIRE | Bool | false | FALSE | False | False | False | False | enable alarm broken wire
|  |  | STIME_RESET | Bool | false | FALSE | False | False | False | False | reset for settling time (external)
|  | Alarm |  | typeAlarm |  |  | False | True | True | False
|  |  | PLCIntern | Byte | 16#0 | 16#10 | False | True | True | False
|  |  | ToSCADA | Byte | 16#0 | 16#11 | False | True | True | False
|  |  | FromSCADA | Byte | 16#0 | 16#12 | False | True | True | False
Element2_OUT |  |  |  | ANA_OUT |  |  | False | True | True | False
|  | Config |  | Struct |  |  | False | False | False | False
|  |  | Enable | Bool | false | FALSE | False | False | False | False | element enabled
|  |  | AOT_Mode | Int | 0 | 0 | False | False | False | False | mode for AOT (1: 4..20mA, 3: P&F)
|  |  | PAW | Int | 0 | 0 | False | False | False | False | PEW of AIN
|  |  | GOP_Open | Bool | false | FALSE | False | False | False | False | limit switch open exists
|  |  | GOS_Closed | Bool | false | FALSE | False | False | False | False | limit switch closeed exists
|  |  | Broken_Wire_Current | Int | 300 | 300 | False | False | False | False | broken wire current (1/100 mA)
|  | STATUS |  | FIX_KEY |  |  | False | True | True | False | status of the measurement
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  |  | OUT_VALUE | Int | 0 | 12 | False | True | True | False | output [0...10000 = 0...100.00%]
|  |  | SERVICE_SET | Int | 0 | 13 | False | True | True | False | service setpoint [0...10000 = 0...100%]
|  |  | SET_VALUE | Int | 0 | 14 | False | True | True | False | FV setpoint from recipe [0...10000 = 0...100%]
|  |  | TIME_OPEN_SET | Int | 0 | 15 | False | True | True | False | max runtime for opening [s]
|  |  | TIME_CLOSE_SET | Int | 0 | 16 | False | True | True | False | max runtime for closing [s]
|  |  | TIME_OPEN_ACT | Int | 0 | 17 | False | True | True | False | act runtime for opening [s]
|  |  | TIME_CLOSE_ACT | Int | 0 | 18 | False | True | True | False | act runtime for closing [s]
|  |  | LOW_RANGE | Int | 0 | 0 | False | False | False | False | low range (output =0)
|  |  | HIGH_RANGE | Int | 10000 | 10000 | False | False | False | False | high range (output = 10000)
|  |  | SETPOINT_AUTO | Int | 0 | 0 | False | False | False | False | setpoint for automatic mode (low range ... high range)
|  |  | SETPOINT_MAN | Int | 0 | 0 | False | False | False | False | setpoint for manual mode (low range ... high range)
|  |  | AUTO_ON | Bool | false | FALSE | False | False | False | False | command for opening in automatic mode
|  |  | MAN_ON | Bool | false | FALSE | False | False | False | False | command for opening in maual mode
|  |  | SERVICE_ON | Bool | false | FALSE | False | False | False | False | command for opening in service mode
|  |  | IS_OPEN | Bool | false | FALSE | False | False | False | False | DIN is open
|  |  | IS_CLOSED | Bool | false | FALSE | False | False | False | False | DIN is closed
|  |  | VALVE_OUT | Bool | false | FALSE | False | False | False | False | DOT for VALVE_OUT
|  |  | KEEP_CLOSED | Bool | false | FALSE | False | False | False | False | keep closed (for bed burst)
|  | Alarm |  | typeAlarm |  |  | False | True | True | False
|  |  | PLCIntern | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | ToSCADA | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | FromSCADA | Byte | 16#0 | 16#00 | False | True | True | False
| Element2_VALUE |  |  | ANA_VALUE |  |  | False | True | True | False
|  | Config |  | Struct |  |  | False | False | False | False
|  |  | Enable | Bool | false | FALSE | False | False | False | False | element enabled
|  |  | AIN_Mode | Int | 1 | 1 | False | False | False | False | mode for AIN (1: 4..20mA, 2: PT100, 3: P&F)
|  |  | PEW | Int | 0 | 0 | False | False | False | False | PEW of AIN
|  |  | Low_Range | Int | 0 | 0 | False | False | False | False | Low Range for analog input
|  |  | High_Range | Int | 1500 | 1500 | False | False | False | False | High Range for analog input
|  |  | Broken_Wire_Current | Int | 300 | 300 | False | False | False | False | broken wire current (1/100 mA)
|  | STATUS |  | FIX_KEY |  |  | False | True | True | False | status of the measurement
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  | SENSOR |  | FIX_KEY |  |  | False | True | True | False | visualize sensor
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  |  | ACT_VALUE | Int | 0 | 0 | False | True | True | False | actual value
|  |  | SET_VALUE | Int | 0 | 0 | False | True | True | False | setpoint from recipe
|  |  | MP_SET_VALUE | Int | 0 | 0 | False | True | True | False | machine paramter setpoint
|  |  | MIN_VALUE | Int | 0 | 0 | False | True | True | False | min limit value
|  |  | MIN_MIN_VALUE | Int | 0 | 0 | False | True | True | False | min min limit value
|  |  | MAX_VALUE | Int | 0 | 0 | False | True | True | False | max limit value
|  |  | MAX_MAX_VALUE | Int | 0 | 0 | False | True | True | False | max max limit value
|  |  | SET_STIME | Int | 180 | 180 | False | True | True | False | setpoint for alarm settling time [s]
|  |  | SET_DTIME_MIN | Int | 30 | 30 | False | True | True | False | setpoint for min alarm delay time [s]
|  |  | SET_DTIME_MAX | Int | 30 | 30 | False | True | True | False | setpoint for max alarm delay time [s]
|  |  | SET_DTIME_BROKEN_WIRE | Int | 5 | 5 | False | True | True | False | setpoint for broken wire alarm delay time [s]
|  |  | ACT_STIME | Int | 0 | 0 | False | True | True | False | actual value of alarm settling time [s]
|  |  | ACT_DTIME_MIN | Int | 0 | 0 | False | True | True | False | actual value of min alarm delay time [s]
|  |  | ACT_DTIME_MAX | Int | 0 | 0 | False | True | True | False | actual value of max alarm delay time [s]
|  |  | ACT_DTIME_BROKEN_WIRE | Int | 0 | 0 | False | True | True | False | actual value of broken wire alarm delay time [s]
|  |  | TRIP_VALUE | Int | 0 | 0 | False | True | True | False | trip value
|  | PID |  | Struct |  |  | False | True | True | False
|  | MANUAL_KEY |  | FIX_KEY |  |  | False | True | True | False | switching to manual mode
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  |  | MODE | Int | 0 | 0 | False | True | True | False | modus controller
|  |  | SET_AUTO | Int | 0 | 0 | False | True | True | False | setpoint (auto) for controller
|  |  | SET_MAN | Int | 0 | 0 | False | True | True | False | output value of controller in manual mode
|  |  | SET_START | Int | 0 | 0 | False | True | True | False | output value of controller in start mode
|  |  | SET_FV | Int | 0 | 0 | False | True | True | False | output value of controller in forced mode
|  |  | SPARE | Int | 0 | 0 | False | True | True | False | output value of controller in revision mode
|  |  | P | Int | 4500 | 4500 | False | True | True | False | PID parameter: P
|  |  | I | Int | 600 | 600 | False | True | True | False | PID parameter: I
|  |  | D | Int | 0 | 0 | False | True | True | False | PID parameter: D
|  |  | CONTRL_OUT | Int | 0 | 0 | False | True | True | False | output of controller (Y)
|  |  | TREND_SET_VALUE | Int | 0 | 0 | False | True | True | False | copy of SET_AUTO for trending
|  |  | CONTRL_ON | Bool | false | FALSE | False | True | True | False | controller is on
|  |  | MAN_ON | Bool | false | FALSE | False | True | True | False | manual mode on
|  |  | START_ON | Bool | false | FALSE | False | True | True | False | start mode on
|  |  | FV_ON | Bool | false | FALSE | False | True | True | False | forced mode on
|  |  | FREZ_ON | Bool | false | FALSE | False | True | True | False | freeze on
|  |  | SERVICE_ON | Bool | false | FALSE | False | True | True | False | service mode on
|  |  | OLD_IN_SET | Int | 0 | 0 | False | False | False | False | old setpoint for min/max alarm check
|  |  | INT_SCALE_OUT | Int | 0 | 0 | False | False | False | False | measurement scale out as integer
|  |  | REAL_SCALE_OUT | Real | 0 | 0 | False | False | False | False | measurement scale out as real
|  |  | BROKEN_WIRE | Bool | false | FALSE | False | False | False | False | wire broken, written in OB35, read in OB1
|  |  | CHK_MIN_0 | Bool | false | FALSE | False | False | False | False | also check if MIN value is "0"
|  |  | CHK_MAX_0 | Bool | false | FALSE | False | False | False | False | also check if MAX value is "0"
|  |  | EN_ALM_MIN | Bool | false | FALSE | False | False | False | False | enable alarm minimum
|  |  | EN_ALM_MIN_MIN | Bool | false | FALSE | False | False | False | False | enable alarm minimum minimum
|  |  | EN_ALM_MAX | Bool | false | FALSE | False | False | False | False | enable alarm maximum
|  |  | EN_ALM_MAX_MAX | Bool | false | FALSE | False | False | False | False | enable alarm maximum maximum
|  |  | EN_ALM_BROKEN_WIRE | Bool | false | FALSE | False | False | False | False | enable alarm broken wire
|  |  | STIME_RESET | Bool | false | FALSE | False | False | False | False | reset for settling time (external)
|  | Alarm |  | typeAlarm |  |  | False | True | True | False
|  |  | PLCIntern | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | ToSCADA | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | FromSCADA | Byte | 16#0 | 16#00 | False | True | True | False
Element3_OUT |  |  |  | ANA_OUT |  |  | False | True | True | False
|  | Config |  | Struct |  |  | False | False | False | False
|  |  | Enable | Bool | false | FALSE | False | False | False | False | element enabled
|  |  | AOT_Mode | Int | 0 | 0 | False | False | False | False | mode for AOT (1: 4..20mA, 3: P&F)
|  |  | PAW | Int | 0 | 0 | False | False | False | False | PEW of AIN
|  |  | GOP_Open | Bool | false | FALSE | False | False | False | False | limit switch open exists
|  |  | GOS_Closed | Bool | false | FALSE | False | False | False | False | limit switch closeed exists
|  |  | Broken_Wire_Current | Int | 300 | 300 | False | False | False | False | broken wire current (1/100 mA)
|  | STATUS |  | FIX_KEY |  |  | False | True | True | False | status of the measurement
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  |  | OUT_VALUE | Int | 0 | 23 | False | True | True | False | output [0...10000 = 0...100.00%]
|  |  | SERVICE_SET | Int | 0 | 24 | False | True | True | False | service setpoint [0...10000 = 0...100%]
|  |  | SET_VALUE | Int | 0 | 25 | False | True | True | False | FV setpoint from recipe [0...10000 = 0...100%]
|  |  | TIME_OPEN_SET | Int | 0 | 26 | False | True | True | False | max runtime for opening [s]
|  |  | TIME_CLOSE_SET | Int | 0 | 27 | False | True | True | False | max runtime for closing [s]
|  |  | TIME_OPEN_ACT | Int | 0 | 28 | False | True | True | False | act runtime for opening [s]
|  |  | TIME_CLOSE_ACT | Int | 0 | 29 | False | True | True | False | act runtime for closing [s]
|  |  | LOW_RANGE | Int | 0 | 0 | False | False | False | False | low range (output =0)
|  |  | HIGH_RANGE | Int | 10000 | 10000 | False | False | False | False | high range (output = 10000)
|  |  | SETPOINT_AUTO | Int | 0 | 0 | False | False | False | False | setpoint for automatic mode (low range ... high range)
|  |  | SETPOINT_MAN | Int | 0 | 0 | False | False | False | False | setpoint for manual mode (low range ... high range)
|  |  | AUTO_ON | Bool | false | FALSE | False | False | False | False | command for opening in automatic mode
|  |  | MAN_ON | Bool | false | FALSE | False | False | False | False | command for opening in maual mode
|  |  | SERVICE_ON | Bool | false | FALSE | False | False | False | False | command for opening in service mode
|  |  | IS_OPEN | Bool | false | FALSE | False | False | False | False | DIN is open
|  |  | IS_CLOSED | Bool | false | FALSE | False | False | False | False | DIN is closed
|  |  | VALVE_OUT | Bool | false | FALSE | False | False | False | False | DOT for VALVE_OUT
|  |  | KEEP_CLOSED | Bool | false | FALSE | False | False | False | False | keep closed (for bed burst)
|  | Alarm |  | typeAlarm |  |  | False | True | True | False
|  |  | PLCIntern | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | ToSCADA | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | FromSCADA | Byte | 16#0 | 16#00 | False | True | True | False
| Element3_VALUE |  |  | ANA_VALUE |  |  | False | True | True | False
|  | Config |  | Struct |  |  | False | False | False | False
|  |  | Enable | Bool | false | FALSE | False | False | False | False | element enabled
|  |  | AIN_Mode | Int | 1 | 1 | False | False | False | False | mode for AIN (1: 4..20mA, 2: PT100, 3: P&F)
|  |  | PEW | Int | 0 | 0 | False | False | False | False | PEW of AIN
|  |  | Low_Range | Int | 0 | 0 | False | False | False | False | Low Range for analog input
|  |  | High_Range | Int | 1500 | 1500 | False | False | False | False | High Range for analog input
|  |  | Broken_Wire_Current | Int | 300 | 300 | False | False | False | False | broken wire current (1/100 mA)
|  | STATUS |  | FIX_KEY |  |  | False | True | True | False | status of the measurement
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  | SENSOR |  | FIX_KEY |  |  | False | True | True | False | visualize sensor
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  |  | ACT_VALUE | Int | 0 | 0 | False | True | True | False | actual value
|  |  | SET_VALUE | Int | 0 | 0 | False | True | True | False | setpoint from recipe
|  |  | MP_SET_VALUE | Int | 0 | 0 | False | True | True | False | machine paramter setpoint
|  |  | MIN_VALUE | Int | 0 | 0 | False | True | True | False | min limit value
|  |  | MIN_MIN_VALUE | Int | 0 | 0 | False | True | True | False | min min limit value
|  |  | MAX_VALUE | Int | 0 | 0 | False | True | True | False | max limit value
|  |  | MAX_MAX_VALUE | Int | 0 | 0 | False | True | True | False | max max limit value
|  |  | SET_STIME | Int | 180 | 180 | False | True | True | False | setpoint for alarm settling time [s]
|  |  | SET_DTIME_MIN | Int | 30 | 30 | False | True | True | False | setpoint for min alarm delay time [s]
|  |  | SET_DTIME_MAX | Int | 30 | 30 | False | True | True | False | setpoint for max alarm delay time [s]
|  |  | SET_DTIME_BROKEN_WIRE | Int | 5 | 5 | False | True | True | False | setpoint for broken wire alarm delay time [s]
|  |  | ACT_STIME | Int | 0 | 0 | False | True | True | False | actual value of alarm settling time [s]
|  |  | ACT_DTIME_MIN | Int | 0 | 0 | False | True | True | False | actual value of min alarm delay time [s]
|  |  | ACT_DTIME_MAX | Int | 0 | 0 | False | True | True | False | actual value of max alarm delay time [s]
|  |  | ACT_DTIME_BROKEN_WIRE | Int | 0 | 0 | False | True | True | False | actual value of broken wire alarm delay time [s]
|  |  | TRIP_VALUE | Int | 0 | 0 | False | True | True | False | trip value
|  | PID |  | Struct |  |  | False | True | True | False
|  | MANUAL_KEY |  | FIX_KEY |  |  | False | True | True | False | switching to manual mode
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  |  | MODE | Int | 0 | 0 | False | True | True | False | modus controller
|  |  | SET_AUTO | Int | 0 | 0 | False | True | True | False | setpoint (auto) for controller
|  |  | SET_MAN | Int | 0 | 0 | False | True | True | False | output value of controller in manual mode
|  |  | SET_START | Int | 0 | 0 | False | True | True | False | output value of controller in start mode
|  |  | SET_FV | Int | 0 | 0 | False | True | True | False | output value of controller in forced mode
|  |  | SPARE | Int | 0 | 0 | False | True | True | False | output value of controller in revision mode
|  |  | P | Int | 4500 | 4500 | False | True | True | False | PID parameter: P
|  |  | I | Int | 600 | 600 | False | True | True | False | PID parameter: I
|  |  | D | Int | 0 | 0 | False | True | True | False | PID parameter: D
|  |  | CONTRL_OUT | Int | 0 | 0 | False | True | True | False | output of controller (Y)
|  |  | TREND_SET_VALUE | Int | 0 | 0 | False | True | True | False | copy of SET_AUTO for trending
|  |  | CONTRL_ON | Bool | false | FALSE | False | True | True | False | controller is on
|  |  | MAN_ON | Bool | false | FALSE | False | True | True | False | manual mode on
|  |  | START_ON | Bool | false | FALSE | False | True | True | False | start mode on
|  |  | FV_ON | Bool | false | FALSE | False | True | True | False | forced mode on
|  |  | FREZ_ON | Bool | false | FALSE | False | True | True | False | freeze on
|  |  | SERVICE_ON | Bool | false | FALSE | False | True | True | False | service mode on
|  |  | OLD_IN_SET | Int | 0 | 0 | False | False | False | False | old setpoint for min/max alarm check
|  |  | INT_SCALE_OUT | Int | 0 | 0 | False | False | False | False | measurement scale out as integer
|  |  | REAL_SCALE_OUT | Real | 0 | 0 | False | False | False | False | measurement scale out as real
|  |  | BROKEN_WIRE | Bool | false | FALSE | False | False | False | False | wire broken, written in OB35, read in OB1
|  |  | CHK_MIN_0 | Bool | false | FALSE | False | False | False | False | also check if MIN value is "0"
|  |  | CHK_MAX_0 | Bool | false | FALSE | False | False | False | False | also check if MAX value is "0"
|  |  | EN_ALM_MIN | Bool | false | FALSE | False | False | False | False | enable alarm minimum
|  |  | EN_ALM_MIN_MIN | Bool | false | FALSE | False | False | False | False | enable alarm minimum minimum
|  |  | EN_ALM_MAX | Bool | false | FALSE | False | False | False | False | enable alarm maximum
|  |  | EN_ALM_MAX_MAX | Bool | false | FALSE | False | False | False | False | enable alarm maximum maximum
|  |  | EN_ALM_BROKEN_WIRE | Bool | false | FALSE | False | False | False | False | enable alarm broken wire
|  |  | STIME_RESET | Bool | false | FALSE | False | False | False | False | reset for settling time (external)
|  | Alarm |  | typeAlarm |  |  | False | True | True | False
|  |  | PLCIntern | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | ToSCADA | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | FromSCADA | Byte | 16#0 | 16#00 | False | True | True | False
Element4_OUT |  |  |  | ANA_OUT |  |  | False | True | True | False
|  | Config |  | Struct |  |  | False | False | False | False
|  |  | Enable | Bool | false | FALSE | False | False | False | False | element enabled
|  |  | AOT_Mode | Int | 0 | 0 | False | False | False | False | mode for AOT (1: 4..20mA, 3: P&F)
|  |  | PAW | Int | 0 | 0 | False | False | False | False | PEW of AIN
|  |  | GOP_Open | Bool | false | FALSE | False | False | False | False | limit switch open exists
|  |  | GOS_Closed | Bool | false | FALSE | False | False | False | False | limit switch closeed exists
|  |  | Broken_Wire_Current | Int | 300 | 300 | False | False | False | False | broken wire current (1/100 mA)
|  | STATUS |  | FIX_KEY |  |  | False | True | True | False | status of the measurement
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  |  | OUT_VALUE | Int | 0 | 34 | False | True | True | False | output [0...10000 = 0...100.00%]
|  |  | SERVICE_SET | Int | 0 | 35 | False | True | True | False | service setpoint [0...10000 = 0...100%]
|  |  | SET_VALUE | Int | 0 | 36 | False | True | True | False | FV setpoint from recipe [0...10000 = 0...100%]
|  |  | TIME_OPEN_SET | Int | 0 | 37 | False | True | True | False | max runtime for opening [s]
|  |  | TIME_CLOSE_SET | Int | 0 | 38 | False | True | True | False | max runtime for closing [s]
|  |  | TIME_OPEN_ACT | Int | 0 | 39 | False | True | True | False | act runtime for opening [s]
|  |  | TIME_CLOSE_ACT | Int | 0 | 40 | False | True | True | False | act runtime for closing [s]
|  |  | LOW_RANGE | Int | 0 | 0 | False | False | False | False | low range (output =0)
|  |  | HIGH_RANGE | Int | 10000 | 10000 | False | False | False | False | high range (output = 10000)
|  |  | SETPOINT_AUTO | Int | 0 | 0 | False | False | False | False | setpoint for automatic mode (low range ... high range)
|  |  | SETPOINT_MAN | Int | 0 | 0 | False | False | False | False | setpoint for manual mode (low range ... high range)
|  |  | AUTO_ON | Bool | false | FALSE | False | False | False | False | command for opening in automatic mode
|  |  | MAN_ON | Bool | false | FALSE | False | False | False | False | command for opening in maual mode
|  |  | SERVICE_ON | Bool | false | FALSE | False | False | False | False | command for opening in service mode
|  |  | IS_OPEN | Bool | false | FALSE | False | False | False | False | DIN is open
|  |  | IS_CLOSED | Bool | false | FALSE | False | False | False | False | DIN is closed
|  |  | VALVE_OUT | Bool | false | FALSE | False | False | False | False | DOT for VALVE_OUT
|  |  | KEEP_CLOSED | Bool | false | FALSE | False | False | False | False | keep closed (for bed burst)
|  | Alarm |  | typeAlarm |  |  | False | True | True | False
|  |  | PLCIntern | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | ToSCADA | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | FromSCADA | Byte | 16#0 | 16#00 | False | True | True | False
| Element4_VALUE |  |  | ANA_VALUE |  |  | False | True | True | False
|  | Config |  | Struct |  |  | False | False | False | False
|  |  | Enable | Bool | false | FALSE | False | False | False | False | element enabled
|  |  | AIN_Mode | Int | 1 | 1 | False | False | False | False | mode for AIN (1: 4..20mA, 2: PT100, 3: P&F)
|  |  | PEW | Int | 0 | 0 | False | False | False | False | PEW of AIN
|  |  | Low_Range | Int | 0 | 0 | False | False | False | False | Low Range for analog input
|  |  | High_Range | Int | 1500 | 1500 | False | False | False | False | High Range for analog input
|  |  | Broken_Wire_Current | Int | 300 | 300 | False | False | False | False | broken wire current (1/100 mA)
|  | STATUS |  | FIX_KEY |  |  | False | True | True | False | status of the measurement
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  | SENSOR |  | FIX_KEY |  |  | False | True | True | False | visualize sensor
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  |  | ACT_VALUE | Int | 0 | 0 | False | True | True | False | actual value
|  |  | SET_VALUE | Int | 0 | 0 | False | True | True | False | setpoint from recipe
|  |  | MP_SET_VALUE | Int | 0 | 0 | False | True | True | False | machine paramter setpoint
|  |  | MIN_VALUE | Int | 0 | 0 | False | True | True | False | min limit value
|  |  | MIN_MIN_VALUE | Int | 0 | 0 | False | True | True | False | min min limit value
|  |  | MAX_VALUE | Int | 0 | 0 | False | True | True | False | max limit value
|  |  | MAX_MAX_VALUE | Int | 0 | 0 | False | True | True | False | max max limit value
|  |  | SET_STIME | Int | 180 | 180 | False | True | True | False | setpoint for alarm settling time [s]
|  |  | SET_DTIME_MIN | Int | 30 | 30 | False | True | True | False | setpoint for min alarm delay time [s]
|  |  | SET_DTIME_MAX | Int | 30 | 30 | False | True | True | False | setpoint for max alarm delay time [s]
|  |  | SET_DTIME_BROKEN_WIRE | Int | 5 | 5 | False | True | True | False | setpoint for broken wire alarm delay time [s]
|  |  | ACT_STIME | Int | 0 | 0 | False | True | True | False | actual value of alarm settling time [s]
|  |  | ACT_DTIME_MIN | Int | 0 | 0 | False | True | True | False | actual value of min alarm delay time [s]
|  |  | ACT_DTIME_MAX | Int | 0 | 0 | False | True | True | False | actual value of max alarm delay time [s]
|  |  | ACT_DTIME_BROKEN_WIRE | Int | 0 | 0 | False | True | True | False | actual value of broken wire alarm delay time [s]
|  |  | TRIP_VALUE | Int | 0 | 0 | False | True | True | False | trip value
|  | PID |  | Struct |  |  | False | True | True | False
|  | MANUAL_KEY |  | FIX_KEY |  |  | False | True | True | False | switching to manual mode
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  |  | MODE | Int | 0 | 0 | False | True | True | False | modus controller
|  |  | SET_AUTO | Int | 0 | 0 | False | True | True | False | setpoint (auto) for controller
|  |  | SET_MAN | Int | 0 | 0 | False | True | True | False | output value of controller in manual mode
|  |  | SET_START | Int | 0 | 0 | False | True | True | False | output value of controller in start mode
|  |  | SET_FV | Int | 0 | 0 | False | True | True | False | output value of controller in forced mode
|  |  | SPARE | Int | 0 | 0 | False | True | True | False | output value of controller in revision mode
|  |  | P | Int | 4500 | 4500 | False | True | True | False | PID parameter: P
|  |  | I | Int | 600 | 600 | False | True | True | False | PID parameter: I
|  |  | D | Int | 0 | 0 | False | True | True | False | PID parameter: D
|  |  | CONTRL_OUT | Int | 0 | 0 | False | True | True | False | output of controller (Y)
|  |  | TREND_SET_VALUE | Int | 0 | 0 | False | True | True | False | copy of SET_AUTO for trending
|  |  | CONTRL_ON | Bool | false | FALSE | False | True | True | False | controller is on
|  |  | MAN_ON | Bool | false | FALSE | False | True | True | False | manual mode on
|  |  | START_ON | Bool | false | FALSE | False | True | True | False | start mode on
|  |  | FV_ON | Bool | false | FALSE | False | True | True | False | forced mode on
|  |  | FREZ_ON | Bool | false | FALSE | False | True | True | False | freeze on
|  |  | SERVICE_ON | Bool | false | FALSE | False | True | True | False | service mode on
|  |  | OLD_IN_SET | Int | 0 | 0 | False | False | False | False | old setpoint for min/max alarm check
|  |  | INT_SCALE_OUT | Int | 0 | 0 | False | False | False | False | measurement scale out as integer
|  |  | REAL_SCALE_OUT | Real | 0 | 0 | False | False | False | False | measurement scale out as real
|  |  | BROKEN_WIRE | Bool | false | FALSE | False | False | False | False | wire broken, written in OB35, read in OB1
|  |  | CHK_MIN_0 | Bool | false | FALSE | False | False | False | False | also check if MIN value is "0"
|  |  | CHK_MAX_0 | Bool | false | FALSE | False | False | False | False | also check if MAX value is "0"
|  |  | EN_ALM_MIN | Bool | false | FALSE | False | False | False | False | enable alarm minimum
|  |  | EN_ALM_MIN_MIN | Bool | false | FALSE | False | False | False | False | enable alarm minimum minimum
|  |  | EN_ALM_MAX | Bool | false | FALSE | False | False | False | False | enable alarm maximum
|  |  | EN_ALM_MAX_MAX | Bool | false | FALSE | False | False | False | False | enable alarm maximum maximum
|  |  | EN_ALM_BROKEN_WIRE | Bool | false | FALSE | False | False | False | False | enable alarm broken wire
|  |  | STIME_RESET | Bool | false | FALSE | False | False | False | False | reset for settling time (external)
|  | Alarm |  | typeAlarm |  |  | False | True | True | False
|  |  | PLCIntern | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | ToSCADA | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | FromSCADA | Byte | 16#0 | 16#00 | False | True | True | False
Element5_OUT |  |  |  | ANA_OUT |  |  | False | True | True | False
|  | Config |  | Struct |  |  | False | False | False | False
|  |  | Enable | Bool | false | FALSE | False | False | False | False | element enabled
|  |  | AOT_Mode | Int | 0 | 0 | False | False | False | False | mode for AOT (1: 4..20mA, 3: P&F)
|  |  | PAW | Int | 0 | 0 | False | False | False | False | PEW of AIN
|  |  | GOP_Open | Bool | false | FALSE | False | False | False | False | limit switch open exists
|  |  | GOS_Closed | Bool | false | FALSE | False | False | False | False | limit switch closeed exists
|  |  | Broken_Wire_Current | Int | 300 | 300 | False | False | False | False | broken wire current (1/100 mA)
|  | STATUS |  | FIX_KEY |  |  | False | True | True | False | status of the measurement
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  |  | OUT_VALUE | Int | 0 | 45 | False | True | True | False | output [0...10000 = 0...100.00%]
|  |  | SERVICE_SET | Int | 0 | 46 | False | True | True | False | service setpoint [0...10000 = 0...100%]
|  |  | SET_VALUE | Int | 0 | 47 | False | True | True | False | FV setpoint from recipe [0...10000 = 0...100%]
|  |  | TIME_OPEN_SET | Int | 0 | 48 | False | True | True | False | max runtime for opening [s]
|  |  | TIME_CLOSE_SET | Int | 0 | 49 | False | True | True | False | max runtime for closing [s]
|  |  | TIME_OPEN_ACT | Int | 0 | 50 | False | True | True | False | act runtime for opening [s]
|  |  | TIME_CLOSE_ACT | Int | 0 | 51 | False | True | True | False | act runtime for closing [s]
|  |  | LOW_RANGE | Int | 0 | 0 | False | False | False | False | low range (output =0)
|  |  | HIGH_RANGE | Int | 10000 | 10000 | False | False | False | False | high range (output = 10000)
|  |  | SETPOINT_AUTO | Int | 0 | 0 | False | False | False | False | setpoint for automatic mode (low range ... high range)
|  |  | SETPOINT_MAN | Int | 0 | 0 | False | False | False | False | setpoint for manual mode (low range ... high range)
|  |  | AUTO_ON | Bool | false | FALSE | False | False | False | False | command for opening in automatic mode
|  |  | MAN_ON | Bool | false | FALSE | False | False | False | False | command for opening in maual mode
|  |  | SERVICE_ON | Bool | false | FALSE | False | False | False | False | command for opening in service mode
|  |  | IS_OPEN | Bool | false | FALSE | False | False | False | False | DIN is open
|  |  | IS_CLOSED | Bool | false | FALSE | False | False | False | False | DIN is closed
|  |  | VALVE_OUT | Bool | false | FALSE | False | False | False | False | DOT for VALVE_OUT
|  |  | KEEP_CLOSED | Bool | false | FALSE | False | False | False | False | keep closed (for bed burst)
|  | Alarm |  | typeAlarm |  |  | False | True | True | False
|  |  | PLCIntern | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | ToSCADA | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | FromSCADA | Byte | 16#0 | 16#00 | False | True | True | False
| Element5_VALUE |  |  | ANA_VALUE |  |  | False | True | True | False
|  | Config |  | Struct |  |  | False | False | False | False
|  |  | Enable | Bool | false | FALSE | False | False | False | False | element enabled
|  |  | AIN_Mode | Int | 1 | 1 | False | False | False | False | mode for AIN (1: 4..20mA, 2: PT100, 3: P&F)
|  |  | PEW | Int | 0 | 0 | False | False | False | False | PEW of AIN
|  |  | Low_Range | Int | 0 | 0 | False | False | False | False | Low Range for analog input
|  |  | High_Range | Int | 1500 | 1500 | False | False | False | False | High Range for analog input
|  |  | Broken_Wire_Current | Int | 300 | 300 | False | False | False | False | broken wire current (1/100 mA)
|  | STATUS |  | FIX_KEY |  |  | False | True | True | False | status of the measurement
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  | SENSOR |  | FIX_KEY |  |  | False | True | True | False | visualize sensor
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  |  | ACT_VALUE | Int | 0 | 0 | False | True | True | False | actual value
|  |  | SET_VALUE | Int | 0 | 0 | False | True | True | False | setpoint from recipe
|  |  | MP_SET_VALUE | Int | 0 | 0 | False | True | True | False | machine paramter setpoint
|  |  | MIN_VALUE | Int | 0 | 0 | False | True | True | False | min limit value
|  |  | MIN_MIN_VALUE | Int | 0 | 0 | False | True | True | False | min min limit value
|  |  | MAX_VALUE | Int | 0 | 0 | False | True | True | False | max limit value
|  |  | MAX_MAX_VALUE | Int | 0 | 0 | False | True | True | False | max max limit value
|  |  | SET_STIME | Int | 180 | 180 | False | True | True | False | setpoint for alarm settling time [s]
|  |  | SET_DTIME_MIN | Int | 30 | 30 | False | True | True | False | setpoint for min alarm delay time [s]
|  |  | SET_DTIME_MAX | Int | 30 | 30 | False | True | True | False | setpoint for max alarm delay time [s]
|  |  | SET_DTIME_BROKEN_WIRE | Int | 5 | 5 | False | True | True | False | setpoint for broken wire alarm delay time [s]
|  |  | ACT_STIME | Int | 0 | 0 | False | True | True | False | actual value of alarm settling time [s]
|  |  | ACT_DTIME_MIN | Int | 0 | 0 | False | True | True | False | actual value of min alarm delay time [s]
|  |  | ACT_DTIME_MAX | Int | 0 | 0 | False | True | True | False | actual value of max alarm delay time [s]
|  |  | ACT_DTIME_BROKEN_WIRE | Int | 0 | 0 | False | True | True | False | actual value of broken wire alarm delay time [s]
|  |  | TRIP_VALUE | Int | 0 | 0 | False | True | True | False | trip value
|  | PID |  | Struct |  |  | False | True | True | False
|  | MANUAL_KEY |  | FIX_KEY |  |  | False | True | True | False | switching to manual mode
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  |  | MODE | Int | 0 | 0 | False | True | True | False | modus controller
|  |  | SET_AUTO | Int | 0 | 0 | False | True | True | False | setpoint (auto) for controller
|  |  | SET_MAN | Int | 0 | 0 | False | True | True | False | output value of controller in manual mode
|  |  | SET_START | Int | 0 | 0 | False | True | True | False | output value of controller in start mode
|  |  | SET_FV | Int | 0 | 0 | False | True | True | False | output value of controller in forced mode
|  |  | SPARE | Int | 0 | 0 | False | True | True | False | output value of controller in revision mode
|  |  | P | Int | 4500 | 4500 | False | True | True | False | PID parameter: P
|  |  | I | Int | 600 | 600 | False | True | True | False | PID parameter: I
|  |  | D | Int | 0 | 0 | False | True | True | False | PID parameter: D
|  |  | CONTRL_OUT | Int | 0 | 0 | False | True | True | False | output of controller (Y)
|  |  | TREND_SET_VALUE | Int | 0 | 0 | False | True | True | False | copy of SET_AUTO for trending
|  |  | CONTRL_ON | Bool | false | FALSE | False | True | True | False | controller is on
|  |  | MAN_ON | Bool | false | FALSE | False | True | True | False | manual mode on
|  |  | START_ON | Bool | false | FALSE | False | True | True | False | start mode on
|  |  | FV_ON | Bool | false | FALSE | False | True | True | False | forced mode on
|  |  | FREZ_ON | Bool | false | FALSE | False | True | True | False | freeze on
|  |  | SERVICE_ON | Bool | false | FALSE | False | True | True | False | service mode on
|  |  | OLD_IN_SET | Int | 0 | 0 | False | False | False | False | old setpoint for min/max alarm check
|  |  | INT_SCALE_OUT | Int | 0 | 0 | False | False | False | False | measurement scale out as integer
|  |  | REAL_SCALE_OUT | Real | 0 | 0 | False | False | False | False | measurement scale out as real
|  |  | BROKEN_WIRE | Bool | false | FALSE | False | False | False | False | wire broken, written in OB35, read in OB1
|  |  | CHK_MIN_0 | Bool | false | FALSE | False | False | False | False | also check if MIN value is "0"
|  |  | CHK_MAX_0 | Bool | false | FALSE | False | False | False | False | also check if MAX value is "0"
|  |  | EN_ALM_MIN | Bool | false | FALSE | False | False | False | False | enable alarm minimum
|  |  | EN_ALM_MIN_MIN | Bool | false | FALSE | False | False | False | False | enable alarm minimum minimum
|  |  | EN_ALM_MAX | Bool | false | FALSE | False | False | False | False | enable alarm maximum
|  |  | EN_ALM_MAX_MAX | Bool | false | FALSE | False | False | False | False | enable alarm maximum maximum
|  |  | EN_ALM_BROKEN_WIRE | Bool | false | FALSE | False | False | False | False | enable alarm broken wire
|  |  | STIME_RESET | Bool | false | FALSE | False | False | False | False | reset for settling time (external)
|  | Alarm |  | typeAlarm |  |  | False | True | True | False
|  |  | PLCIntern | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | ToSCADA | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | FromSCADA | Byte | 16#0 | 16#00 | False | True | True | False
Element6_OUT |  |  |  | ANA_OUT |  |  | False | True | True | False
|  | Config |  | Struct |  |  | False | False | False | False
|  |  | Enable | Bool | false | FALSE | False | False | False | False | element enabled
|  |  | AOT_Mode | Int | 0 | 0 | False | False | False | False | mode for AOT (1: 4..20mA, 3: P&F)
|  |  | PAW | Int | 0 | 0 | False | False | False | False | PEW of AIN
|  |  | GOP_Open | Bool | false | FALSE | False | False | False | False | limit switch open exists
|  |  | GOS_Closed | Bool | false | FALSE | False | False | False | False | limit switch closeed exists
|  |  | Broken_Wire_Current | Int | 300 | 300 | False | False | False | False | broken wire current (1/100 mA)
|  | STATUS |  | FIX_KEY |  |  | False | True | True | False | status of the measurement
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  |  | OUT_VALUE | Int | 0 | 56 | False | True | True | False | output [0...10000 = 0...100.00%]
|  |  | SERVICE_SET | Int | 0 | 57 | False | True | True | False | service setpoint [0...10000 = 0...100%]
|  |  | SET_VALUE | Int | 0 | 58 | False | True | True | False | FV setpoint from recipe [0...10000 = 0...100%]
|  |  | TIME_OPEN_SET | Int | 0 | 59 | False | True | True | False | max runtime for opening [s]
|  |  | TIME_CLOSE_SET | Int | 0 | 60 | False | True | True | False | max runtime for closing [s]
|  |  | TIME_OPEN_ACT | Int | 0 | 61 | False | True | True | False | act runtime for opening [s]
|  |  | TIME_CLOSE_ACT | Int | 0 | 62 | False | True | True | False | act runtime for closing [s]
|  |  | LOW_RANGE | Int | 0 | 0 | False | False | False | False | low range (output =0)
|  |  | HIGH_RANGE | Int | 10000 | 10000 | False | False | False | False | high range (output = 10000)
|  |  | SETPOINT_AUTO | Int | 0 | 0 | False | False | False | False | setpoint for automatic mode (low range ... high range)
|  |  | SETPOINT_MAN | Int | 0 | 0 | False | False | False | False | setpoint for manual mode (low range ... high range)
|  |  | AUTO_ON | Bool | false | FALSE | False | False | False | False | command for opening in automatic mode
|  |  | MAN_ON | Bool | false | FALSE | False | False | False | False | command for opening in maual mode
|  |  | SERVICE_ON | Bool | false | FALSE | False | False | False | False | command for opening in service mode
|  |  | IS_OPEN | Bool | false | FALSE | False | False | False | False | DIN is open
|  |  | IS_CLOSED | Bool | false | FALSE | False | False | False | False | DIN is closed
|  |  | VALVE_OUT | Bool | false | FALSE | False | False | False | False | DOT for VALVE_OUT
|  |  | KEEP_CLOSED | Bool | false | FALSE | False | False | False | False | keep closed (for bed burst)
|  | Alarm |  | typeAlarm |  |  | False | True | True | False
|  |  | PLCIntern | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | ToSCADA | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | FromSCADA | Byte | 16#0 | 16#00 | False | True | True | False
| Element6_VALUE |  |  | ANA_VALUE |  |  | False | True | True | False
|  | Config |  | Struct |  |  | False | False | False | False
|  |  | Enable | Bool | false | FALSE | False | False | False | False | element enabled
|  |  | AIN_Mode | Int | 1 | 1 | False | False | False | False | mode for AIN (1: 4..20mA, 2: PT100, 3: P&F)
|  |  | PEW | Int | 0 | 0 | False | False | False | False | PEW of AIN
|  |  | Low_Range | Int | 0 | 0 | False | False | False | False | Low Range for analog input
|  |  | High_Range | Int | 1500 | 1500 | False | False | False | False | High Range for analog input
|  |  | Broken_Wire_Current | Int | 300 | 300 | False | False | False | False | broken wire current (1/100 mA)
|  | STATUS |  | FIX_KEY |  |  | False | True | True | False | status of the measurement
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  | SENSOR |  | FIX_KEY |  |  | False | True | True | False | visualize sensor
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  |  | ACT_VALUE | Int | 0 | 0 | False | True | True | False | actual value
|  |  | SET_VALUE | Int | 0 | 0 | False | True | True | False | setpoint from recipe
|  |  | MP_SET_VALUE | Int | 0 | 0 | False | True | True | False | machine paramter setpoint
|  |  | MIN_VALUE | Int | 0 | 0 | False | True | True | False | min limit value
|  |  | MIN_MIN_VALUE | Int | 0 | 0 | False | True | True | False | min min limit value
|  |  | MAX_VALUE | Int | 0 | 0 | False | True | True | False | max limit value
|  |  | MAX_MAX_VALUE | Int | 0 | 0 | False | True | True | False | max max limit value
|  |  | SET_STIME | Int | 180 | 180 | False | True | True | False | setpoint for alarm settling time [s]
|  |  | SET_DTIME_MIN | Int | 30 | 30 | False | True | True | False | setpoint for min alarm delay time [s]
|  |  | SET_DTIME_MAX | Int | 30 | 30 | False | True | True | False | setpoint for max alarm delay time [s]
|  |  | SET_DTIME_BROKEN_WIRE | Int | 5 | 5 | False | True | True | False | setpoint for broken wire alarm delay time [s]
|  |  | ACT_STIME | Int | 0 | 0 | False | True | True | False | actual value of alarm settling time [s]
|  |  | ACT_DTIME_MIN | Int | 0 | 0 | False | True | True | False | actual value of min alarm delay time [s]
|  |  | ACT_DTIME_MAX | Int | 0 | 0 | False | True | True | False | actual value of max alarm delay time [s]
|  |  | ACT_DTIME_BROKEN_WIRE | Int | 0 | 0 | False | True | True | False | actual value of broken wire alarm delay time [s]
|  |  | TRIP_VALUE | Int | 0 | 0 | False | True | True | False | trip value
|  | PID |  | Struct |  |  | False | True | True | False
|  | MANUAL_KEY |  | FIX_KEY |  |  | False | True | True | False | switching to manual mode
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  |  | MODE | Int | 0 | 0 | False | True | True | False | modus controller
|  |  | SET_AUTO | Int | 0 | 0 | False | True | True | False | setpoint (auto) for controller
|  |  | SET_MAN | Int | 0 | 0 | False | True | True | False | output value of controller in manual mode
|  |  | SET_START | Int | 0 | 0 | False | True | True | False | output value of controller in start mode
|  |  | SET_FV | Int | 0 | 0 | False | True | True | False | output value of controller in forced mode
|  |  | SPARE | Int | 0 | 0 | False | True | True | False | output value of controller in revision mode
|  |  | P | Int | 4500 | 4500 | False | True | True | False | PID parameter: P
|  |  | I | Int | 600 | 600 | False | True | True | False | PID parameter: I
|  |  | D | Int | 0 | 0 | False | True | True | False | PID parameter: D
|  |  | CONTRL_OUT | Int | 0 | 0 | False | True | True | False | output of controller (Y)
|  |  | TREND_SET_VALUE | Int | 0 | 0 | False | True | True | False | copy of SET_AUTO for trending
|  |  | CONTRL_ON | Bool | false | FALSE | False | True | True | False | controller is on
|  |  | MAN_ON | Bool | false | FALSE | False | True | True | False | manual mode on
|  |  | START_ON | Bool | false | FALSE | False | True | True | False | start mode on
|  |  | FV_ON | Bool | false | FALSE | False | True | True | False | forced mode on
|  |  | FREZ_ON | Bool | false | FALSE | False | True | True | False | freeze on
|  |  | SERVICE_ON | Bool | false | FALSE | False | True | True | False | service mode on
|  |  | OLD_IN_SET | Int | 0 | 0 | False | False | False | False | old setpoint for min/max alarm check
|  |  | INT_SCALE_OUT | Int | 0 | 0 | False | False | False | False | measurement scale out as integer
|  |  | REAL_SCALE_OUT | Real | 0 | 0 | False | False | False | False | measurement scale out as real
|  |  | BROKEN_WIRE | Bool | false | FALSE | False | False | False | False | wire broken, written in OB35, read in OB1
|  |  | CHK_MIN_0 | Bool | false | FALSE | False | False | False | False | also check if MIN value is "0"
|  |  | CHK_MAX_0 | Bool | false | FALSE | False | False | False | False | also check if MAX value is "0"
|  |  | EN_ALM_MIN | Bool | false | FALSE | False | False | False | False | enable alarm minimum
|  |  | EN_ALM_MIN_MIN | Bool | false | FALSE | False | False | False | False | enable alarm minimum minimum
|  |  | EN_ALM_MAX | Bool | false | FALSE | False | False | False | False | enable alarm maximum
|  |  | EN_ALM_MAX_MAX | Bool | false | FALSE | False | False | False | False | enable alarm maximum maximum
|  |  | EN_ALM_BROKEN_WIRE | Bool | false | FALSE | False | False | False | False | enable alarm broken wire
|  |  | STIME_RESET | Bool | false | FALSE | False | False | False | False | reset for settling time (external)
|  | Alarm |  | typeAlarm |  |  | False | True | True | False
|  |  | PLCIntern | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | ToSCADA | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | FromSCADA | Byte | 16#0 | 16#00 | False | True | True | False
Element7_OUT |  |  |  | ANA_OUT |  |  | False | True | True | False
|  | MANUAL_KEY |  | FIX_KEY |  |  | False | True | True | False | switching to manual mode
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  |  | MODE | Int | 0 | 0 | False | True | True | False | modus controller
|  |  | SET_AUTO | Int | 0 | 0 | False | True | True | False | setpoint (auto) for controller
|  |  | SET_MAN | Int | 0 | 0 | False | True | True | False | output value of controller in manual mode
|  |  | SET_START | Int | 0 | 0 | False | True | True | False | output value of controller in start mode
|  |  | SET_FV | Int | 0 | 0 | False | True | True | False | output value of controller in forced mode
|  |  | SPARE | Int | 0 | 0 | False | True | True | False | output value of controller in revision mode
|  |  | P | Int | 4500 | 4500 | False | True | True | False | PID parameter: P
|  |  | I | Int | 600 | 600 | False | True | True | False | PID parameter: I
|  |  | D | Int | 0 | 0 | False | True | True | False | PID parameter: D
|  |  | CONTRL_OUT | Int | 0 | 0 | False | True | True | False | output of controller (Y)
|  |  | TREND_SET_VALUE | Int | 0 | 0 | False | True | True | False | copy of SET_AUTO for trending
|  |  | CONTRL_ON | Bool | false | FALSE | False | True | True | False | controller is on
|  |  | MAN_ON | Bool | false | FALSE | False | True | True | False | manual mode on
|  |  | START_ON | Bool | false | FALSE | False | True | True | False | start mode on
|  |  | FV_ON | Bool | false | FALSE | False | True | True | False | forced mode on
|  |  | FREZ_ON | Bool | false | FALSE | False | True | True | False | freeze on
|  |  | SERVICE_ON | Bool | false | FALSE | False | True | True | False | service mode on
|  |  | OLD_IN_SET | Int | 0 | 0 | False | False | False | False | old setpoint for min/max alarm check
|  |  | INT_SCALE_OUT | Int | 0 | 0 | False | False | False | False | measurement scale out as integer
|  |  | REAL_SCALE_OUT | Real | 0 | 0 | False | False | False | False | measurement scale out as real
|  |  | BROKEN_WIRE | Bool | false | FALSE | False | False | False | False | wire broken, written in OB35, read in OB1
|  |  | CHK_MIN_0 | Bool | false | FALSE | False | False | False | False | also check if MIN value is "0"
|  |  | CHK_MAX_0 | Bool | false | FALSE | False | False | False | False | also check if MAX value is "0"
|  |  | EN_ALM_MIN | Bool | false | FALSE | False | False | False | False | enable alarm minimum
|  |  | EN_ALM_MIN_MIN | Bool | false | FALSE | False | False | False | False | enable alarm minimum minimum
|  |  | EN_ALM_MAX | Bool | false | FALSE | False | False | False | False | enable alarm maximum
|  |  | EN_ALM_MAX_MAX | Bool | false | FALSE | False | False | False | False | enable alarm maximum maximum
|  |  | EN_ALM_BROKEN_WIRE | Bool | false | FALSE | False | False | False | False | enable alarm broken wire
|  |  | STIME_RESET | Bool | false | FALSE | False | False | False | False | reset for settling time (external)
|  | Alarm |  | typeAlarm |  |  | False | True | True | False
|  |  | PLCIntern | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | ToSCADA | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | FromSCADA | Byte | 16#0 | 16#00 | False | True | True | False
Element7_OUT |  |  |  | ANA_OUT |  |  | False | True | True | False
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  | SENSOR |  | FIX_KEY |  |  | False | True | True | False | visualize sensor
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  |  | ACT_VALUE | Int | 0 | 0 | False | True | True | False | actual value
|  |  | SET_VALUE | Int | 0 | 0 | False | True | True | False | setpoint from recipe
|  |  | MP_SET_VALUE | Int | 0 | 0 | False | True | True | False | machine paramter setpoint
|  |  | MIN_VALUE | Int | 0 | 0 | False | True | True | False | min limit value
|  |  | MIN_MIN_VALUE | Int | 0 | 0 | False | True | True | False | min min limit value
|  |  | MAX_VALUE | Int | 0 | 0 | False | True | True | False | max limit value
|  |  | MAX_MAX_VALUE | Int | 0 | 0 | False | True | True | False | max max limit value
|  |  | SET_STIME | Int | 180 | 180 | False | True | True | False | setpoint for alarm settling time [s]
|  |  | SET_DTIME_MIN | Int | 30 | 30 | False | True | True | False | setpoint for min alarm delay time [s]
|  |  | SET_DTIME_MAX | Int | 30 | 30 | False | True | True | False | setpoint for max alarm delay time [s]
|  |  | SET_DTIME_BROKEN_WIRE | Int | 5 | 5 | False | True | True | False | setpoint for broken wire alarm delay time [s]
|  |  | ACT_STIME | Int | 0 | 0 | False | True | True | False | actual value of alarm settling time [s]
|  |  | ACT_DTIME_MIN | Int | 0 | 0 | False | True | True | False | actual value of min alarm delay time [s]
|  |  | ACT_DTIME_MAX | Int | 0 | 0 | False | True | True | False | actual value of max alarm delay time [s]
|  |  | ACT_DTIME_BROKEN_WIRE | Int | 0 | 0 | False | True | True | False | actual value of broken wire alarm delay time [s]
|  |  | TRIP_VALUE | Int | 0 | 0 | False | True | True | False | trip value
|  | PID |  | Struct |  |  | False | True | True | False
|  | MANUAL_KEY |  | FIX_KEY |  |  | False | True | True | False | switching to manual mode
|  |  | motor_forward | Bool | false | FALSE | False | True | True | False | motor movement forward
|  |  | key_on | Bool | false | FALSE | False | True | True | False | signal from FIX: switch on
|  |  | UGU_off | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching off is not enabled
|  |  | UGU_on | Bool | false | FALSE | False | True | True | False | impulse: display userguide, why switching on is not enabled
|  |  | isoff | Bool | false | FALSE | False | True | True | False | signal to FIX: display off/deflated/closed
|  |  | ison | Bool | false | FALSE | False | True | True | False | signal to FIX: display on/inflated/open
|  |  | isalarm | Bool | false | FALSE | False | True | True | False | signal to FIX: display red blinking
|  |  | isalarm_sens | Bool | false | FALSE | False | True | True | False | signal to FIX: sensor red blinking
|  |  | ena_off | Bool | false | FALSE | False | True | True | False | enable switching off
|  |  | ena_on | Bool | false | FALSE | False | True | True | False | enable switching on
|  |  | ena_key_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | ena_key_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_off | Bool | false | FALSE | False | True | True | False | internal
|  |  | imp_on | Bool | false | FALSE | False | True | True | False | internal
|  |  | cmd_off | Bool | false | FALSE | False | True | True | False | switched off
|  |  | cmd_on | Bool | false | FALSE | False | True | True | False | switched on
|  |  | MODE | Int | 0 | 0 | False | True | True | False | modus controller
|  |  | SET_AUTO | Int | 0 | 0 | False | True | True | False | setpoint (auto) for controller
|  |  | SET_MAN | Int | 0 | 0 | False | True | True | False | output value of controller in manual mode
|  |  | SET_START | Int | 0 | 0 | False | True | True | False | output value of controller in start mode
|  |  | SET_FV | Int | 0 | 0 | False | True | True | False | output value of controller in forced mode
|  |  | SPARE | Int | 0 | 0 | False | True | True | False | output value of controller in revision mode
|  |  | P | Int | 4500 | 4500 | False | True | True | False | PID parameter: P
|  |  | I | Int | 600 | 600 | False | True | True | False | PID parameter: I
|  |  | D | Int | 0 | 0 | False | True | True | False | PID parameter: D
|  |  | CONTRL_OUT | Int | 0 | 0 | False | True | True | False | output of controller (Y)
|  |  | TREND_SET_VALUE | Int | 0 | 0 | False | True | True | False | copy of SET_AUTO for trending
|  |  | CONTRL_ON | Bool | false | FALSE | False | True | True | False | controller is on
|  |  | MAN_ON | Bool | false | FALSE | False | True | True | False | manual mode on
|  |  | START_ON | Bool | false | FALSE | False | True | True | False | start mode on
|  |  | FV_ON | Bool | false | FALSE | False | True | True | False | forced mode on
|  |  | FREZ_ON | Bool | false | FALSE | False | True | True | False | freeze on
|  |  | SERVICE_ON | Bool | false | FALSE | False | True | True | False | service mode on
|  |  | OLD_IN_SET | Int | 0 | 0 | False | False | False | False | old setpoint for min/max alarm check
|  |  | INT_SCALE_OUT | Int | 0 | 0 | False | False | False | False | measurement scale out as integer
|  |  | REAL_SCALE_OUT | Real | 0 | 0 | False | False | False | False | measurement scale out as real
|  |  | BROKEN_WIRE | Bool | false | FALSE | False | False | False | False | wire broken, written in OB35, read in OB1
|  |  | CHK_MIN_0 | Bool | false | FALSE | False | False | False | False | also check if MIN value is "0"
|  |  | CHK_MAX_0 | Bool | false | FALSE | False | False | False | False | also check if MAX value is "0"
|  |  | EN_ALM_MIN | Bool | false | FALSE | False | False | False | False | enable alarm minimum
|  |  | EN_ALM_MIN_MIN | Bool | false | FALSE | False | False | False | False | enable alarm minimum minimum
|  |  | EN_ALM_MAX | Bool | false | FALSE | False | False | False | False | enable alarm maximum
|  |  | EN_ALM_MAX_MAX | Bool | false | FALSE | False | False | False | False | enable alarm maximum maximum
|  |  | EN_ALM_BROKEN_WIRE | Bool | false | FALSE | False | False | False | False | enable alarm broken wire
|  |  | STIME_RESET | Bool | false | FALSE | False | False | False | False | reset for settling time (external)
|  | Alarm |  | typeAlarm |  |  | False | True | True | False
|  |  | PLCIntern | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | ToSCADA | Byte | 16#0 | 16#00 | False | True | True | False
|  |  | FromSCADA | Byte | 16#0 | 16#00 | False | True | True | False

## Tabelle2
Frame 18: 747 | 747 | 747
Frame 23: 685 | 685 | 685
Frame 28: 673 | 673 | 673
Frame 33: 715 | 715 | 715
Frame 38: 735 | 735 | 735
Frame 43: 658 | 658 | 658
Frame 48: 670 | 670 | 670
Frame 53: 754 | 754 | 754
Frame 61: 651 | 651 | 651
Frame 66: 663 | 663 | 663
Frame 69: 192 | 192 | 192
7143
0.28951
0.51043
0.22092
18
69
51